In this section, we present three different approaches to conducting a sensitivity analysis for Option D:

* Local One-step-at-a-time (OAT) sampling analysis
* Global OAT screening method
* Global Regression based analysis

# I. Various Sensitivity Analysis Methods

## CASE A- New Construction of a Medium Office

### 1. Situation

This example involves the new construction of a medium office building in San Francisco, CA. The sensitivity of the following building characteristics is unknown and will be characterized with respect to whole building Electric Energy Use Intensity (EUI):

* Window to Wall Ratio (WWR)
* Lighting Power Density (LPD)
* Space Infiltration

### 2. Building Modeling and Analysis Tools

For this example, the OpenStudio[[1]](#footnote-1) (OS) tool chain will be used since it is free and open source. Building Energy Models (BEM) created in the OpenStudio format (.osm) can easily be manipulated by OpenStudio Measures,[[2]](#footnote-2) which are a set of programmatic instructions written in the Ruby programming language that makes changes to an energy model. These model changes can be as simple as changing an existing parameter in the model (Ex, change chiller COP) or as complicated as changing the entire HVAC system for a building. This concept of creating and manipulating energy models through OpenStudio Measures will allow us to turn building characteristics into variables and determine their sensitivity in a way that is consistent, scalable and easily shared with co-workers, clients or the general public.

The *Medium Office* from the DOE Commercial Prototype Building Models[[3]](#footnote-3) will serve as our example building and the energy model will be programmatically generated using the OpenStudio Prototype Buildings Measure.[[4]](#footnote-4) This has the advantage that the reader can easily reproduce the workflow used to create the model and results shown in this section.

The sensitivity analyses presented utilize the OpenStudio Analysis Spreadsheet[[5]](#footnote-5) for problem definition and the cloud computing capabilities of OpenStudio Server[[6]](#footnote-6) for algorithm implementation and simulation runs. Both of these tools are free to use, however the actual cloud computing time from Amazon must be purchased from a user specific Amazon cloud computing account (Amazon EC2).


### 3. Energy Model and Variable Characterization

The energy model for this example is created by using the following inputs in the Prototype Building Measure:

* Building Type: Medium Office
* Vintage: 90.1-2010
* Climate Zone: ASHRAE 169-2006-3C

This results in a building that is *typical* of a new construction, medium office building in San Francisco, CA and is depicted in Figure 1.

Figure 1: Medium Office Prototype Building



The building characteristics of Window to Wall Ratio, Lighting Power Density and Space Infiltration will be altered by using OpenStudio Measures that specifically manipulate those values in the energy model. The actual OpenStudio Measures used in this example, along with the code used in this analysis can be downloaded from (XXX). To understand the effect that these parameters have on building Electric EUI, we first need to define valid ranges (minimum and maximum) and distributions (triangular, uniform, etc.) for each input, thus turning our previously static building parameters into dynamic variables that the sampling based algorithms will vary.

For this example, triangular distributions were chosen for each variable as a demonstration since they are easily definable and are depicted in Figures 2-4 with the ranges listed in Table 1. The OpenStudio Analysis Spreadsheet allows for triangular, normal, log-normal and uniform distribution types. Ranges and distribution types for each variable are typically defined by project constraints or best practices. It should be noted that while the plotted distributions in Figures 2-4 do not appear to be triangles, that is just an artifact of plotting them using histogram and curve fit functions in R.

Table 1: Explanatory Variable Ranges

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Variable | | Minimum | Mode | Maximum |
| Lighting Power Density (W/ft2) | 0.2 | | 0.6 | 1 |
| Window to Wall Ratio (fraction) | 0.2 | | 0.33 | 0.4 |
| Space Infiltration (% change) | -30 | | 0 | 30 |

The distributions for LPD and WWR specify actual LPD and WWR parameter values respectively, while the distribution for Space Infiltration represents a percent change from the Space Infiltration value that is in the baseline model. This is done to be consistent with how each OpenStudio Measure implements the desired variable change in the model. The OpenStudio Measures for LPD and WWR apply an actual value of these parameters to the model, while the Space Infiltration Measure applies a percent change to the baseline models value. Some analysts like to deal with absolutes, while others like to deal with percent changes. Neither way is incorrect, however, care must be taken to be aware and consistent with how each OpenStudio Measure operates.

Figure 2: Lighting Power Density Distribution




Figure 3: Space Infiltration Percent Change Distribution





Figure 4: Window to Wall Ratio



### 4. Local One-step-at-a-time (OAT) sampling analysis

Latin Hypercube Sampling[[7]](#footnote-7) (LHS) attempts to distribute samples evenly over the sample space and can be applied to multiple variables or dimensions. The method essentially divides the distribution to be sampled into areas of equal probability and places an equal number of points into each area. This has the effect of giving a more even sampling across a distribution with fewer points compared to a purely random sample.

Using the OpenStudio Analysis Workflow we will sample the three variables, one at a time, while holding the others constant (at their default values) resulting in an OAT sampling method. This method is also described as a local method since we are holding all the non-sampled variables to their default values. Thus, while we are getting some sense of the effect of the perturbed variable, this perturbation is only with respect to the same locally fixed values for the other variables. The details on how to accomplish this can be found in the user guide for the OpenStudio Analysis Spreadsheet[[8]](#footnote-8) and the actual spreadsheet used in this example can be found here.

Choosing the “correct” number of samples to use in the LHS method is very problem dependent. For example, a smooth linear problem would require very few samples to understand the variation in the output, while a highly nonlinear problem would require “lots” of points to characterize the nonlinear behavior of the problem. It is typical under these conditions to do a grid refinement study where a small number of points are chosen and used, and then twice as many points are used, and then twice again, this process repeating until the variation or characterization of the outputs becomes “good enough” for us to have confidence that we have chosen the “right” number of points. For illustration purposes, the number of samples in this example for each variable was chosen to be 100. This resulted in a total of 300 simulations to run (100 points x 3 variables = 300 total runs) and the solution space is depicted in the parallel coordinates plot in Figure 5. The first three coordinates are the variables: Space Infiltration, LPD and WWR. The fourth coordinate is the dependent variable Electric EUI.

To visually estimate the relative sensitivity of each variable, we can restrict the parallel coordinates plot to display the results of only one of the sampled variables at a time and examine the resulting spread in the Electric EUI. This is depicted in Figures 6-8 for the variables: Space Infiltration reduction, LPD and WWR respectively.

While this method only provides a visual estimation of the variable sensitives, it is nonetheless very powerful and instructive. Examining the Electric EUI coordinate on the far right in Figures 6-8 we can conclude that LPD is the most sensitive with respect to Electric EUI, followed by WWR and then Space Infiltration. This is due to the largest span of Electric EUI values is in Figure 7, which is the case when only LPD was varied. The second largest span of Electric EUI was Figure 8, which is the case when only WWR was varied. Last is Figure 6, the case when Space Infiltration was varied, which has the smallest variation in Electric EUI.

Figure 5: LHS OAT Solution Space




Figure 6: Space Infiltration Reduction (%).

Smallest variation in Electric EUI (MJ/m2)




Figure 7: LPD (W/ft2). Largest variation in Electric EUI (MJ/m2)






Figure 8: WWR (fraction). Medium variation in Electric EUI (MJ/m2)



This visual inspection can be followed up by overlaying the resulting histograms of Electric EUI variation due to the variation in the variables which is depicted in Figure 9. The sensitivity of each variable on Electric EUI can be determined by looking at the support or base width of each colored distribution. For example, the green distribution is the Electric EUI variation resulting from the distribution of LPD given in Figure 2. The blue distribution is the Electric EUI variation resulting from the distribution of Space Infiltration Percent Change in Figure 3 and so on. It should be noted that the height of the distributions are such that the area under the distribution equals one so that each is a probability distribution which makes direct comparison easier.

Figure 9: Electric EUI (MJ/m2) Variation due to Variables




### 5. Global OAT screening method

To gain a more qualitative assessment of the sensitivity of each variable, we will use the Morris OAT Method.[[9]](#footnote-9) Morris’s elementary effects screening method identifies the few important factors or elementary effects (EE) at a cost of r × (p + 1) simulations (where *p* is the number of factors (in this example there are 3 factors or variables) and *r* is the number of EE computed per factor). The EE for each factor or variable is essentially a first order numerical derivative of the output variable of interest (in this example it is Electric EUI) with respect to the factor. Thus the EE calculates the finite-difference of the output variable changes when the input factor is varied at specific points in the parameter space. This calculation is repeated *r* times at different locations in the parameter space to get a global sense of how sensitive each factor or input variable is with respect to the outputs. The Morris Method implementation used in the OpenStudio Server comes from the R package *Sensitivity,* which includes improvements to the original method defined by Morris, specifically a space-filling optimization of the design[[10]](#footnote-10) and a simplex-based design.[[11]](#footnote-11)

For illustrative purposes, the *r* value for this example was set to 10 resulting in a total number of 40 simulations. The resulting sampling pattern of the solution space is plotted in Figure 10. Since *r* was set to 10 for this example, there will be 10 calculations of the EE for the variables, with each one coming from a *different initial condition* in the solution space (computed by various algorithmic settings) depicted in Figure 10, thus making the method more global in nature. Typically *r* is chosen between 4-10, depending on the number of variables and the computational cost of the model.

Figure 10: Sampling pattern for Morris Method



The main output of the Morris Method is the mean and standard deviation of the EEs for each variable. In this example, the 10 EEs are averaged and the standard deviation is computed and denoted µ and σ, respectively. It is typical to take the absolute value of the EEs before averaging to eliminate any possible canceling of values if the EE results are both positive and negative. This is the typical output value for the Morris Method and is denoted µ\* along with the value of σ which characterizes the variation of the EEs. A low value of σ typically means the EE value is relatively consistent and that there is negligible interaction with other possible factors or variables. A higher σ value typically means the EE value is not consistent and there could be nonlinear effects at play and/or there are possible interactive effects with other factors or variables.

The µ\* values for our example are plotted in Figure 11 and µ\* vs σ are plotted in Figure 12. The bars in Figure 11 are just the µ\* values of our input variables and indicates that LPD has the largest EE, followed by WWR and Space Infiltration. Figure 12 is a way to investigate the variation of the EE values for each variable. A low value of σ represents small variations in EE values suggesting there is a linear nature to the variable. A larger value of σ suggests that there may be non-linear effects and/or interactive effects with other parameters. From Figure 12 we can conclude that Space Infiltration has negligible effect on Electric EUI, LPD has the largest effect on Electric EUI and is somewhat linear, and finally WWR has the second largest effect on Electric EUI. In addition, there is indication of interactive effects and/or nonlinear behavior with the WWR variable, due to its higher σ value.

It is noted that these values are consistent with the results of the LHS OAT method previously described, however the results were computed with fewer simulations and the sensitivities are global for the Morris Method, rather than local as was computed with the LHS OAT method. This global nature of the Morris Method is due in part to the computing of the EE over the full range of values of the variables, while the LHS OAT method computes changes with respect to the baseline variable values only.

Like all screening tools, the Morris Method provides qualitative sensitivity measures which allows us to rank the variable in order of importance, but do not quantify exactly the relative importance of the inputs. This means we can only compare and rank results from this example to itself and does not directly translate to other examples or projects.

Figure 11: Average value of Elementary Effects from Morris Method





Figure 12: µ\* vs σ. X1 is Space Infiltration, X2 is LPD and X3 is WWR




### 6. Global Regression based analysis

In this section, we attempt to estimate the sensitivities of the Explanatory Variables by constructing a multi-variable linear model. The model we propose is as follows:

In this model, the slope or beta coefficients (except the intercept ) are a measure of the sensitivity of each variable. As we saw in the previous two methods, LPD had a larger effect on the Electric EUI than WWR, thus in this equation we would expect to be larger than . In fact, we expect that since Space Infiltration had the smallest effect on Electric EUI. To create the data necessary to examine such a model, we will again resort to using LHS, however this time we will **not** do a OAT method but instead sample **all** the Explanatory Variables at the **same** time. For illustrative purposes, we will use 400 as the sample size with the resulting solution space depicted in Figure 13. This solution space is much denser than the OAT LHS sampling depicted in Figure 5.

Figure 13: LHS non-OAT Solution Space



After running the 400 samples using OS Server, an R data frame can easily be obtained by clicking the *download R data frame (Results)* button on OS Server as depicted in Figure 13. To do the linear regression, we use the *lm* function in R. The results of the linear regression are listed in Tables 2-3. As detailed in Chapter (XXX), the results of Table 3 suggest the linear regression is a good fit to the data and the sensitivities or slopes for each Variable align with the results of the previous methods.

Figure 13: Download R dataframe from OS Server




Table 2: Linear Regression Coefficients

|  |  |  |  |
| --- | --- | --- | --- |
| Variable | | Estimate of Beta | Pr value |
|
| Lighting Power Reduction (W/ft2) | 113.62 | | < 2e-16 |
| Window to Wall Ratio (fraction) | 17.07 | | < 2e-16 |
| Space Infiltration (% change) | -0.003 | | 0.0372 |
| (intercept) | 206.67 | | < 2e-16 |

Table 3: Linear Regression Characteristics

|  |  |  |
| --- | --- | --- |
| R-squared Value | | 0.9994 |
| p-value | < 2.2e-16 | |

The final equation for the regression, using rounded values from Table 2, is as follows:

Equation:

1. https://www.OpenStudio.net [↑](#footnote-ref-1)
2. http://nrel.github.io/OpenStudio-user-documentation/getting\_started/about\_measures/ [↑](#footnote-ref-2)
3. https://www.energycodes.gov/commercial-prototype-building-models [↑](#footnote-ref-3)
4. https://github.com/NREL/OpenStudio-Prototype-Buildings [↑](#footnote-ref-4)
5. https://github.com/NREL/OpenStudio-analysis-spreadsheet [↑](#footnote-ref-5)
6. https://github.com/NREL/OpenStudio-server [↑](#footnote-ref-6)
7. M. Mckay, R. Beckman and W. Conover, “A comparison of three methods for selecting values of input variables in the analysis of output from a computer code,” Technometrics, vol. 21, no. 2, pp. 239-245, May. 1979 [↑](#footnote-ref-7)
8. https://github.com/NREL/OpenStudio-analysis-spreadsheet/tree/develop/documentation [↑](#footnote-ref-8)
9. Morris, M.D. (1991). "Factorial Sampling Plans for Preliminary Computational Experiments" (PDF). Technometrics 33: 161–174. [↑](#footnote-ref-9)
10. F. Campolongo, J. Cariboni and A. Saltelli, 2007, An effective screening design for sensitivity,

    Environmental Modelling \& Software, 22, 1509–1518. [↑](#footnote-ref-10)
11. G. Pujol, 2009, Simplex-based screening designs for estimating metamodels, Reliability Engineering and System Safety 94, 1156–1160. [↑](#footnote-ref-11)